## Updates
Storage technology | Storage technology (short name) | Full abbreviation | Short abbreviation | Discharge duration (hours) | Cost at 10 kW ($/kW) | Cost at 100 kW ($/kW) | Cost at 1 MW ($/kW) | Cost at 10 MW ($/kW) | Cost at 100 MW ($/kW) | Cost at 1 GW ($/kW) | Cost at 10 GW ($/kW) | Round-trip efficiency (%) | Cycle life (# of cycles) | Calendar life (yrs) | Depth of discharge (%) | Capacity at end of life (% of rated) | Response time to full power | Output in electric form | Tech readiness score | Fixed O&M ($/kW-yr) | Variable O&M ($/MWh) | Feas. score for residential | Feas. score for industrial | Feas. score for distribution | Feas. score for transmission | Specific energy (kWh/ton-metric) LO | Specific energy (kWh/ton-metric) HI | Energy density (kWh/m3) LO | Energy density (kWh/m3) HI | Cycle life at 80% DoD (1000 cycles) LO | Cycle life at 80% DoD (1000 cycles) HI | Cycle life at 10% DoD (1000 cycles) LO | Cycle life at 10% DoD (1000 cycles) HI | Round-trip energy efficiency at rated power and 80% DoD LO | Round-trip energy efficiency at rated power and 80% DoD HI | Annual operational losses over equipment rating (kWh/yr/kW) LO | Annual operational losses over equipment rating (kWh/yr/kW) HI | Annual maintenance or warranty cost ($/yr/kW) LO | Annual maintenance or warranty cost ($/yr/kW) HI | AC storage unit price at factory (equipment cost) ($/kW) LO | AC storage unit price at factory (equipment cost) ($/kW) HI | Installation cost at residential/small commercial up to 100 kW ($/kW) LO | Installation cost at residential/small commercial up to 100 kW ($/kW) HI | Residential/small commercial up to 100 kW feas. score for installation cost | Installation cost at commercial/industrial up to 1 MW ($/kW) LO | Installation cost at commercial/industrial up to 1 MW ($/kW) HI | Commercial/industrial up to 1 MW feas. score for installation cost | Installation cost at containers/CES fleet up to 2 MW ($/kW) LO | Installation cost at containers/CES fleet up to 2 MW ($/kW) HI | Containers/CES fleet up to 2 MW feas. score for installation cost | Installation cost at substation (requiring installation) up to 10 MW ($/kW) LO | Installation cost at substation (requiring installation) up to 10 MW ($/kW) HI | Substation (requiring installation) up to 10 MW feas. score for installation cost | Installation cost at central/bulk over 50 MW ($/kW) LO | Installation cost at central/bulk over 50 MW ($/kW) HI | Central/bulk over 50 MW feas. score for installation cost | Feasibility score based on maturity for grid applications | Feasibility score based on ability to meet application requirements in Group 1 | Feasibility score based on ability to meet application requirements in Group 2 | Feasibility score based on ability to meet application requirements in Group 3 | Feasibility score based on ability to meet application requirements in Group 4 | Replacement time (years) | Replacement cost (as % of cap. cost) | Footprint (m2/MWh) LO | Footprint (m2/MWh) HI
Lithium-ion iron phosphate - 2 hr | Lithium-ion iron phosphate | LIB-LFP-02 | LIB-LFP | 2 | 1037 | 1037 | 1037 | 922 | 854 | NA | NA | 86 | 2000 | 10 | 80 | 80 | ms | Yes | 1 |  | 0.5125 | 1 | 1 | 0.8 | 0.3
Lithium-ion iron phosphate - 4 hr | Lithium-ion iron phosphate | LIB-LFP-04 | LIB-LFP | 4 | 1793 | 1793 | 1793 | 1643 | 1541 | NA | NA | 86 | 2000 | 10 | 80 | 80 | ms | Yes | 1 |  | 0.5125 | 1 | 1 | 0.8 | 0.3
Lithium-ion iron phosphate - 6 hr | Lithium-ion iron phosphate | LIB-LFP-06 | LIB-LFP | 6 | 2541 | 2541 | 2541 | 2355 | 2220 | NA | NA | 86 | 2000 | 10 | 80 | 80 | ms | Yes | 1 |  | 0.5125 | 1 | 1 | 0.8 | 0.3
Lithium-ion iron phosphate - 8 hr | Lithium-ion iron phosphate | LIB-LFP-08 | LIB-LFP | 8 | 3284 | 3284 | 3284 | 3063 | 2894 | NA | NA | 86 | 2000 | 10 | 80 | 80 | ms | Yes | 1 |  | 0.5125 | 1 | 1 | 0.8 | 0.3
Lithium-ion iron phosphate - 10 hr | Lithium-ion iron phosphate | LIB-LFP-10 | LIB-LFP | 10 | 4023 | 4023 | 4023 | 3767 | 3565 | NA | NA | 86 | 2000 | 10 | 80 | 80 | ms | Yes | 1 |  | 0.5125 | 1 | 1 | 0.8 | 0.3
Lithium-ion nickel-manganese-cobalt - 2 hr | Lithium-ion nickel-manganese-cobalt | LIB-NMC-02 | LIB-NMC | 2 | 1060 | 1060 | 1060 | 944 | 875 | NA | NA | 86 | 1200 | 10 | 80 | 80 | ms | Yes | 1 |  | 0.5125 | 1 | 1 | 0.8 | 0.3
Lithium-ion nickel-manganese-cobalt - 4 hr | Lithium-ion nickel-manganese-cobalt | LIB-NMC-04 | LIB-NMC | 4 | 1838 | 1838 | 1838 | 1685 | 1581 | NA | NA | 86 | 1200 | 10 | 80 | 80 | ms | Yes | 1 |  | 0.5125 | 1 | 1 | 0.8 | 0.3
Lithium-ion nickel-manganese-cobalt - 6 hr | Lithium-ion nickel-manganese-cobalt | LIB-NMC-06 | LIB-NMC | 6 | 2608 | 2608 | 2608 | 2419 | 2280 | NA | NA | 86 | 1200 | 10 | 80 | 80 | ms | Yes | 1 |  | 0.5125 | 1 | 1 | 0.8 | 0.3
Lithium-ion nickel-manganese-cobalt - 8 hr | Lithium-ion nickel-manganese-cobalt | LIB-NMC-08 | LIB-NMC | 8 | 3372 | 3372 | 3372 | 3147 | 2974 | NA | NA | 86 | 1200 | 10 | 80 | 80 | ms | Yes | 1 |  | 0.5125 | 1 | 1 | 0.8 | 0.3
Lithium-ion nickel-manganese-cobalt - 10 hr | Lithium-ion nickel-manganese-cobalt | LIB-NMC-10 | LIB-NMC | 10 | 4132 | 4132 | 4132 | 3871 | 3664 | NA | NA | 86 | 1200 | 10 | 80 | 80 | ms | Yes | 1 |  | 0.5125 | 1 | 1 | 0.8 | 0.3
Lithium-ion - 0.5 hr | Lithium-ion | LIB-00 | LIB | 0.5 | 699.45 | 699.45 | 503.65 | 424.9 | 404.25 | NA | NA | 82 | 2000 | 10 | 80 | 80 | ms | Yes | 1 |  | 0.5125 | 0.3 | 0.6 | 0.8 | 0.5
Lithium-ion - 1 hr | Lithium-ion | LIB-01 | LIB | 1 | 755.2 | 755.2 | 592.3 | 485.5 | 466.3 | NA | NA | 82 | 2000 | 10 | 80 | 80 | ms | Yes | 1 |  | 0.5125 | 0.3 | 0.6 | 0.8 | 0.5
Lithium-ion - 2 hr | Lithium-ion | LIB-02 | LIB | 2 | 2115.6 | 1438.8 | 1117.8 | 949.2 | 903.6 | NA | NA | 86 | 2000 | 10 | 80 | 80 | ms | Yes | 1 |  | 0.5125 | 1 | 1 | 0.8 | 0.3
Lithium-ion - 3 hr | Lithium-ion | LIB-03 | LIB | 3 | 2711.7 | 2038.5 | 1606.5 | 1349.7 | 1287.9 | NA | NA | 86 | 2000 | 10 | 80 | 80 | ms | Yes | 1 |  | 0.5125 | 1 | 1 | 0.8 | 0.3
Lithium-ion - 4 hr | Lithium-ion | LIB-04 | LIB | 4 | 3469.6 | 2638.4 | 2095.2 | 1762.4 | 1680.4 | NA | NA | 86 | 2000 | 10 | 80 | 80 | ms | Yes | 1 |  | 0.5125 | 1 | 1 | 0.8 | 0.3
Lithium-ion - 5 hr | Lithium-ion | LIB-05 | LIB | 5 | 4146.5 | 3238 | 2584 | 2175 | 2052.5 | NA | NA | 86 | 2000 | 10 | 80 | 80 | ms | Yes | 1 |  | 0.5125 | 1 | 1 | 0.8 | 0.3
Lithium-ion - 6 hr | Lithium-ion | LIB-06 | LIB | 6 | 4823.4 | 3837.6 | 3072.6 | 2587.2 | 2440.8 | NA | NA | 86 | 2000 | 10 | 80 | 80 | ms | Yes | 1 |  | 0.5125 | 1 | 1 | 0.8 | 0.3
Lithium-ion - 7 hr | Lithium-ion | LIB-07 | LIB | 7 | 5500.6 | 4435.2 | 3561.6 | 3000.2 | 2829.4 | NA | NA | 86 | 2000 | 10 | 80 | 80 | ms | Yes | 1 |  | 0.5125 | 1 | 1 | 0.8 | 0.3
Lithium-ion - 8 hr | Lithium-ion | LIB-08 | LIB | 8 | 6177.6 | 5036.8 | 4050.4 | 3412.8 | 3217.6 | NA | NA | 86 | 2000 | 10 | 80 | 80 | ms | Yes | 1 |  | 0.5125 | 1 | 1 | 0.8 | 0.3
Lead-acid - 2 hr | Lead-acid | Pb-02 | Pb | 2 | 1065 | 1065 | 1065 | 950 | 873 | NA | NA | 77 | 862 | 12 | 58 |  | ms | Yes | 0.8 |  | 0.5125 | 0.8 | 0.8 | 0.5 | 0.1
Lead-acid - 4 hr | Lead-acid | Pb-04 | Pb | 4 | 1808 | 1808 | 1808 | 1567 | 1544 | NA | NA | 79 | 739 | 12 | 67 |  | ms | Yes | 0.8 |  | 0.5125 | 0.8 | 0.8 | 0.5 | 0.1
Lead-acid - 6 hr | Lead-acid | Pb-06 | Pb | 6 | 2552 | 2552 | 2552 | 2364 | 2215 | NA | NA | 82 | 675 | 12 | 73 |  | ms | Yes | 0.8 |  | 0.5125 | 0.8 | 0.8 | 0.5 | 0.1
Lead-acid - 8 hr | Lead-acid | Pb-08 | Pb | 8 | 3296 | 3296 | 3296 | 3072 | 2886 | NA | NA | 83.5 | 635 | 12 | 78 |  | ms | Yes | 0.8 |  | 0.5125 | 0.8 | 0.8 | 0.5 | 0.1
Lead-acid - 10 hr | Lead-acid | Pb-10 | Pb | 10 | 4040 | 4040 | 4040 | 3780 | 3558 | NA | NA | 85 | 599 | 12 | 82 |  | ms | Yes | 0.8 |  | 0.5125 | 0.8 | 0.8 | 0.5 | 0.1
Lead-carbon - 2 hr | Lead-carbon | PbC-02 | PbC | 2 | 2403.2 | 1755.6 | 1441.8 | NA | NA | NA | NA | 80 | 862 |  |  |  | ms | Yes | 0.8 |  | 0.5125 | 0.8 | 0.8 | 0.5 | 0.1
Lead-carbon - 3 hr | Lead-carbon | PbC-03 | PbC | 3 | 2921.4 | 2215.2 | 1794.3 | NA | NA | NA | NA | 80 | 800 |  |  |  | ms | Yes | 0.8 |  | 0.5125 | 0.8 | 0.8 | 0.5 | 0.1
Lead-carbon - 4 hr | Lead-carbon | PbC-04 | PbC | 4 | 3420 | 2657.6 | 2190 | NA | NA | NA | NA | 80 | 739 |  |  |  | ms | Yes | 0.8 |  | 0.5125 | 0.8 | 0.8 | 0.5 | 0.1
Vanadium redox flow - 2 hr | Vanadium redox flow | VRFB-02 | VRFB | 2 | 1693 | 1693 | 1693 | 1546 | 1438 | NA | NA | 68 | 5201 | 15 | 100 | 100 | ms | Yes | 0.6 |  | 0.5125 | 0 | 0.5 | 0.6 | 0.3
Vanadium redox flow - 4 hr | Vanadium redox flow | VRFB-04 | VRFB | 4 | 3452 | 3452 | 2404 | 2216 | 2070 | NA | NA | 68 | 5201 | 15 | 100 | 100 | ms | Yes | 0.6 |  | 0.5125 | 0 | 0.5 | 0.6 | 0.3
Vanadium redox flow - 6 hr | Vanadium redox flow | VRFB-06 | VRFB | 6 | 4587 | 4587 | 3123 | 2895 | 2710 | NA | NA | 68 | 5201 | 15 | 100 | 100 | ms | Yes | 0.6 |  | 0.5125 | 0 | 0.5 | 0.6 | 0.3
Vanadium redox flow - 8 hr | Vanadium redox flow | VRFB-08 | VRFB | 8 | 4961.6 | 4961.6 | 3845 | 3575 | 3351 | NA | NA | 68 | 5201 | 15 | 100 | 100 | ms | Yes | 0.6 |  | 0.5125 | 0 | 0.5 | 0.6 | 0.3
Vanadium redox flow - 10 hr | Vanadium redox flow | VRFB-10 | VRFB | 10 | 4568 | 4568 | 4568 | 4258 | 3994 | NA | NA | 68 | 5201 | 15 | 100 | 100 | ms | Yes | 0.6 |  | 0.5125 | 0 | 0.5 | 0.6 | 0.3
Flow battery - Zinc bromide - 3 hr | Flow battery - Zinc bromide | FB-ZnBr-03 | FB-ZnBr | 3 | 1429.5 | 1429.5 | NA | NA | NA | NA | NA | 70 | 1500 | 20 | 100 | 100 | ms | Yes | 0.6 |  |  | 0.2 | 0.5 | 0.6 | 0.1
Flow battery - Zinc bromide - 4 hr | Flow battery - Zinc bromide | FB-ZnBr-04 | FB-ZnBr | 4 | 2521.2 | 2521.2 | 2221.2 | 2024 | 1888.8 | NA | NA | 70 | 1500 | 20 | 100 | 100 | ms | Yes | 0.6 |  |  | 0.2 | 0.5 | 0.6 | 0.1
Flow battery - Zinc bromide - 5 hr | Flow battery - Zinc bromide | FB-ZnBr-05 | FB-ZnBr | 5 | 2469.5 | 2469.5 | 2260 | 2147.5 | 2086 | NA | NA | 70 | 1500 | 20 | 100 | 100 | ms | Yes | 0.6 |  |  | 0.2 | 0.5 | 0.6 | 0.1
Flow battery - Zinc bromide - 6 hr | Flow battery - Zinc bromide | FB-ZnBr-06 | FB-ZnBr | 6 | 2915.4 | 2915.4 | 2683.8 | 2554.2 | 2481 | NA | NA | 70 | 1500 | 20 | 100 | 100 | ms | Yes | 0.6 |  |  | 0.2 | 0.5 | 0.6 | 0.1
Flow battery - Iron - 4 hr | Flow battery - Iron | FB-Fe-04 | FB-Fe | 4 | 2020.4 | 2020.4 | 1775.2 | 1665.6 | 1618 | NA | NA | 70 | 1500 | 20 | 100 | 100 | ms | Yes | 0.6 |  |  | 0.2 | 0.5 | 0.6 | 0.1
Flow battery - Iron - 8 hr | Flow battery - Iron | FB-Fe-08 | FB-Fe | 8 | 3507.2 | 3507.2 | 3237.6 | 3056.3 | 2901.6 | NA | NA | 70 | 1500 | 20 | 100 | 100 | ms | Yes | 0.6 |  |  | 0.2 | 0.5 | 0.6 | 0.1
Compressed-air energy storage - 4 hr | Compressed-air energy storage | CAES-04 | CAES | 4 | NA | NA | 1168 | 1168 | 1168 | 1074 | 988 | 52 | 10403 | 40 | 100 | 100 | ms | Yes | 0.8 |  | 0.5125 | 0 | 0 | 0.3 | 1
Compressed-air energy storage - 10 hr | Compressed-air energy storage | CAES-10 | CAES | 10 | NA | NA | 1190 | 1190 | 1190 | 1094 | 1007 | 52 | 10403 | 40 | 100 | 100 | ms | Yes | 0.8 |  | 0.5125 | 0 | 0 | 0.3 | 1
Pumped hydro storage - 4 hr | Pumped hydro storage | PHS-04 | PHS | 4 | NA | NA | 2046 | 2046 | 2046 | 1717 | NA | 80 | 13870 | 40 | 100 | 100 | min | Yes | 1 |  | 0.5125 | 0 | 0 | 0 | 1
Pumped hydro storage - 10 hr | Pumped hydro storage | PHS-10 | PHS | 10 | NA | NA | 2623 | 2623 | 2623 | 2202 | NA | 80 | 13870 | 40 | 100 | 100 | min | Yes | 1 |  | 0.5125 | 0 | 0 | 0 | 1
Nickel - 2 hr | Nickel | Ni-02 | Ni | 2 | 1670.4 | 932.8 | 679.2 | NA | NA | NA | NA | 75 | 1000 | 10 | 80 | 80 | ms | Yes | 0.5 |  |  | 0.3 | 0.3 | 0.3 | 0
Nickel - 3 hr | Nickel | Ni-03 | Ni | 3 | 2224.8 | 1303.2 | 961.5 | NA | NA | NA | NA | 75 | 1000 | 10 | 80 | 80 | ms | Yes | 0.5 |  |  | 0.3 | 0.3 | 0.3 | 0
Nickel - 4 hr | Nickel | Ni-04 | Ni | 4 | 2779.2 | 1674 | 1244 | NA | NA | NA | NA | 75 | 1000 | 10 | 80 | 80 | ms | Yes | 0.5 |  |  | 0.3 | 0.3 | 0.3 | 0
Zinc - 4 hr | Zinc | Zn-04 | Zn | 4 | 1464.4 | 1464.4 | 1242.8 | 1072 | 1008.4 | NA | NA | 75 | 5000 | 15 | 80 | 80 | ms | Yes | 0.3 |  |  | 0.3 | 0.3 | 0.3 | 0
Zinc - 8 hr | Zinc | Zn-08 | Zn | 8 | 2626.4 | 2626.4 | 2355.2 | 2169.6 | NA | NA | NA | 75 | 5000 | 15 | 80 | 80 | ms | Yes | 0.3 |  |  | 0.3 | 0.3 | 0.3 | 0
Flywheel - Long duration - 4 hr | Flywheel - Long duration | FW-LD-04 | FW-LD | 4 | 3900 | 3421.2 | 3013.2 | 2704 | NA | NA | NA | 80 |  | 20 | 100 | 100 | ms | Yes | 0.5 |  |  | 0.2 | 0.4 | 0.9 | 0.8
Flywheel - Short duration | Flywheel - Short duration | FW-SD | FW-SD |  | 1250 | 1250 | 1146.5 | 880 | NA | NA | NA | 80 |  | 20 | 100 | 100 | ms | Yes | 0.8 |  |  | 0.2 | 0.4 | 0.9 | 0.8
Sodium - 6 hr | Sodium | Na-06 | Na | 6 | 2639.4 | 2639.4 | 2639.4 | 2404.2 | 2271 | NA | NA | 75 | 5000 | 15 | 80 | 80 | ms | Yes | 0.8 |  |  | 0 | 1 | 1 | 0.9

## Sheet1
Storage technology | Abbreviation | Discharge duration (hours) LO | Discharge duration (hours) HI | Response time to full power | Output in electric form | Specific energy (kWh/ton-metric) LO | Specific energy (kWh/ton-metric) HI | Energy density (kWh/m3) LO | Energy density (kWh/m3) HI | Cycle life at 80% DoD (1000 cycles) LO | Cycle life at 80% DoD (1000 cycles) HI | Cycle life at 10% DoD (1000 cycles) LO | Cycle life at 10% DoD (1000 cycles) HI | Round-trip energy efficiency at rated power and 80% DoD LO | Round-trip energy efficiency at rated power and 80% DoD HI | Annual operational losses over equipment rating (kWh/yr/kW) LO | Annual operational losses over equipment rating (kWh/yr/kW) HI | Annual maintenance or warranty cost ($/yr/kW) LO | Annual maintenance or warranty cost ($/yr/kW) HI | AC storage unit price at factory (equipment cost) ($/kW) LO | AC storage unit price at factory (equipment cost) ($/kW) HI | Installation cost at residential/small commercial up to 100 kW ($/kW) LO | Installation cost at residential/small commercial up to 100 kW ($/kW) HI | Residential/small commercial up to 100 kW feas. score for installation cost | Installation cost at commercial/industrial up to 1 MW ($/kW) LO | Installation cost at commercial/industrial up to 1 MW ($/kW) HI | Commercial/industrial up to 1 MW feas. score for installation cost | Installation cost at containers/CES fleet up to 2 MW ($/kW) LO | Installation cost at containers/CES fleet up to 2 MW ($/kW) HI | Containers/CES fleet up to 2 MW feas. score for installation cost | Installation cost at substation (requiring installation) up to 10 MW ($/kW) LO | Installation cost at substation (requiring installation) up to 10 MW ($/kW) HI | Substation (requiring installation) up to 10 MW feas. score for installation cost | Installation cost at central/bulk over 50 MW ($/kW) LO | Installation cost at central/bulk over 50 MW ($/kW) HI | Central/bulk over 50 MW feas. score for installation cost | Feasibility score based on maturity for grid applications | Feasibility score based on ability to meet application requirements in Group 1 | Feasibility score based on ability to meet application requirements in Group 2 | Feasibility score based on ability to meet application requirements in Group 3 | Feasibility score based on ability to meet application requirements in Group 4 | Replacement time (years) | Replacement cost (as % of cap. cost) | Footprint (m2/MWh) LO | Footprint (m2/MWh) HI | Maturity (2015 handbook)
Lithium-ion - High Power | LIB-p | 0.25 | 1 | ms | Yes | 60 | 90 | 60 | 90 | 4 | 8 | 60 | 110 | 0.84 | 0.91 | 110 | 250 | 8 | 35 | 800 | 1200 | 300 | 450 | 0.3 | 300 | 500 | 0.6 | 250 | 600 | 1 | 400 | 800 | 0.8 | 250 | 600 | 0.5 | 0.7 | 0 | 0.8 | 0 | 0.8 | 8 | 50 | 40 | 60 | C+
Lithium Ion - High Energy | LIB-e | 1 | 4 | ms | Yes | 80 | 120 | 90 | 130 | 3.5 | 7 | 50 | 100 | 0.85 | 0.92 | 120 | 250 | 7 | 25 | 2500 | 3500 | 400 | 600 | 1 | 500 | 650 | 1 | 300 | 600 | 1 | 500 | 900 | 0.8 | 250 | 600 | 0.3 | 0.6 | 0.7 | 0.5 | 0.6 | 0.4 | 8 | 30 | 18 | 26 | C+
Ni batt. (NiCd, NiZn, NiMH) | Ni-batt | 0.3 | 3 | ms | Yes | 50 | 90 | 40 | 210 | 1 | 3 | 1 | 3 | 0.7 | 0.8 | 150 | 500 | 2.25 | 40.5 | 1100 | 1900 | 300 | 450 | 0.3 | 300 | 700 | 0.3 | 300 | 700 | 0.3 | 500 | 900 | 0.3 | NaN | NaN | 0 | 0.7 | 0.5 | 0.4 | 0.5 | 0.4 | 8 | 30 | 26 | 93
Advanced Lead Acid | LA-adv | 2 | 5 | ms | Yes | 18 | 30 | 30 | 70 | 1.2 | 2.4 | 20 | 30 | 0.8 | 0.9 | 250 | 900 | 10 | 30 | 2200 | 3900 | 500 | 700 | 0.8 | 400 | 700 | 0.8 | 600 | 1200 | 0.5 | 600 | 1100 | 0.5 | 300 | 700 | 0.1 | 0.8 | 0.6 | 0.5 | 0.7 | 1 | 8 | 50 | 33 | 45 | C
Valve Regulated Lead Acid | VRLA | 2 | 4 | ms | Yes | 18 | 25 | 30 | 60 | 0.6 | 1 | 2 | 4 | 0.68 | 0.78 | 300 | 900 | 10 | 40 | 1600 | 2500 | 450 | 650 | 0.8 | 400 | 650 | 0.8 | 550 | 1100 | 0.5 | 550 | 1000 | 0.5 | 300 | 650 | 0.1 | 0.8 | 0.6 | 0.2 | 0.7 | 1 | 6 | 35 | 25 | 35
Vanadium Redox Battery | VRFB | 3 | 5 | ms | Yes | 8 | 11 | 15 | 21 | 6 | 8 | 160 | 200 | 0.58 | 0.68 | 300 | 875 | 9 | 15 | 2200 | 3100 | NaN | NaN | 0 | 600 | 1200 | 0.5 | 600 | 800 | 0.4 | 600 | 1000 | 0.6 | NaN | NaN | 0.3 | 0.5 | 0.6 | 0.3 | 0.6 | 0.2 | 10 | 20 | 37 | 55
Adv.Vanadium Red. Flow Batt. | A-VRFB | 3 | 6 | ms | Yes | 17 | 21 | 25 | 30 | 6 | 8 | 160 | 200 | 0.65 | 0.7 | 100 | 300 | 10 | 14 | 2000 | 2500 | NaN | NaN | 0 | 100 | 200 | 0.5 | 90 | 140 | 0.5 | 100 | 150 | 0.6 | NaN | NaN | 0.3 | 0.5 | 0.6 | 0.3 | 0.6 | 0.2 | 10 | 20 | 17 | 33
Zinc Bromide | ZnBr | 2 | 4 | ms | Yes | 30 | 50 | 30 | 45 | 1.5 | 2.5 | 15 | 25 | 0.62 | 0.7 | 570 | 670 | 10 | 30 | 1200 | 3000 | 800 | 1000 | 0.2 | 300 | 900 | 0.5 | 500 | 600 | 0.4 | 400 | 700 | 0.6 | NaN | NaN | 0.1 | 0.6 | 0.6 | 0.3 | 0.6 | 0.2 | 8 | 20 | 9 | 19 | C-
Sodium Sulfur | NaS | 6 | 7 | ms | Yes | 80 | 140 | 100 | 170 | 5 | 6 | 40 | 50 | 0.73 | 0.8 | 200 | 625 | 15 | 60 | 2600 | 3100 | NaN | NaN | 0 | 600 | 800 | 1 | 1000 | 1100 | 0.2 | 800 | 1000 | 1 | 700 | 800 | 0.9 | 0.9 | 0.9 | 0.6 | 0.7 | 0.6 | 16 | 30 | 4 | 5 | A
Sodium Nickel Chloride | NaNiCl | 2 | 4 | ms | Yes | 100 | 150 | 170 | 190 | 3 | 5 | 50 | 100 | 0.82 | 0.87 | 85 | 145 | 10 | 22 | 2000 | 3000 | 300 | 400 | 0.3 | 400 | 600 | 1 | 300 | 500 | 1 | 300 | 500 | 0.8 | 300 | 500 | 0.2 | 0.7 | 0.7 | 0.6 | 0.6 | 0.6 | 10 | 30 | 8 | 11 | B-
Thermal Storage (Cold) | Ice | 4 | 7 | sec | No | 10 | 20 | 10 | 20 | 5.5 | 11 | 5.5 | 11 | 0.9 | 1 | 0 | 15 | 3 | 15 | 500 | 1300 | NaN | NaN | 0.1 | 500 | 1500 | 0.9 | NaN | NaN | 0 | 500 | 1200 | 0.5 | NaN | NaN | 0 | 0.6 | 0.7 | 0 | 0.4 | 0 | 10 | 30 | 108 | 135
Thermal Storage (Hot) | Heat | 4 | 9 | sec | No | 150 | 160 | 110 | 130 | 3.6 | 3.8 | 7.2 | 7.5 | 0.91 | 0.98 | 30 | 90 | 2 | 12 | 110 | 300 | 100 | 200 | 1 | 100 | 150 | 0.7 | NaN | NaN | 0 | NaN | NaN | 0 | NaN | NaN | 0 | 0.6 | 0.7 | 1 | 0.4 | 0 | 12 | 50 | 11 | 13
Zinc-Air Battery | ZnAir | 5 | 6 | ms | Yes | 130 | 170 | 300 | 500 | 5 | 10 | 10 | 20 | 0.65 | 0.77 | 540 | 750 | 15 | 40 | 1200 | 1400 | 300 | 700 | 0.3 | 500 | 1000 | 0.3 | 300 | 700 | 0.2 | NaN | NaN | 0.3 | NaN | NaN | 0 | 0.2 | 0.3 | 0 | 0.4 | 0.1 | 6 | 50 | 5 | 6 | E
Flywheel | FlyWl | 0.03 | 1 | ms | Yes | 5 | 12 | 5 | 15 | 100 | 200 | 170 | 200 | 0.84 | 0.86 | 750 | 850 | 35 | 50 | 1200 | 1600 | 300 | 600 | 0.2 | 400 | 800 | 0.4 | 400 | 800 | 0.2 | 500 | 800 | 0.9 | 400 | 800 | 0.8 | 0.8 | 0 | 1 | 0 | 0.7 | 10 | 20 | 530 | 670 | C+
Double Layer Capacitors | DL-CAP | 0.08 | 1.2 | ms | Yes | 2.3 | 16 | 2.1 | 15 | 100 | 200 | 100 | 200 | 0.92 | 0.97 | 80 | 250 | 8 | 10 | 600 | 1000 | 100 | 250 | 0 | 400 | 700 | 0.5 | 300 | 450 | 0.2 | 300 | 600 | 0.3 | 200 | 400 | 0.1 | 0.3 | 0 | 0.7 | 0 | 0.6 | 8 | 30 | 100 | 400
Hybrid LA & DL-CAP | Hybrid | 0.5 | 5 | ms | Yes | 16 | 28 | 32 | 65 | 5 | 17.5 | 20 | 70 | 0.82 | 0.87 | 100 | 700 | 5 | 15 | 1000 | 1200 | 400 | 600 | 0.4 | 300 | 650 | 0.7 | 500 | 1000 | 0.7 | 500 | 1000 | 0.6 | 250 | 650 | 0.1 | 0.6 | 0.6 | 0.6 | 0.7 | 0.6 | 8 | 30 | 65 | 150
Compressed-Air ES, cavern | CAES-c | 8 | 10 | min | Yes | NaN | NaN | NaN | NaN | 6 | 12 | 6 | 12 | 0.6 | 0.7 | 300 | 1000 | 3 | 12 | 700 | 1300 | NaN | NaN | 0 | NaN | NaN | 0 | NaN | NaN | 0 | 0 | 0 | 0.3 | 0 | 0 | 1 | 0.8 | 0.8 | 0.1 | 0.5 | 0 | 16 | 10 | NaN | NaN | A
Compressed-Air ES, small | CAES-s | 3 | 5 | sec | Yes | NaN | NaN | NaN | NaN | 10 | 20 | 100 | 200 | 0.6 | 0.7 | 300 | 1000 | 1 | 4 | 1800 | 2100 | NaN | NaN | 0 | 400 | 900 | 0.5 | 250 | 750 | 0.2 | 600 | 900 | 0.8 | NaN | NaN | 0.1 | 0.3 | 0.7 | 0.2 | 0.6 | 0.2 | 16 | 15 | NaN | NaN
Pumped Hydro | P-Hydro | 8 | 10 | min | Yes | NaN | NaN | NaN | NaN | 10 | 12 | 10 | 12 | 0.7 | 0.8 | 200 | 750 | 10 | 60 | 1800 | 2200 | NaN | NaN | 0 | NaN | NaN | 0 | NaN | NaN | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0.9 | 0.2 | 0.5 | 0 | 16 | 5 | NaN | NaN | A